## Sayfa1
ONGAS 600P Serisi |  | ONGAS 604 P | ONGAS 605 P | ONGAS 606 P | ONGAS 607 P | ONGAS 608 P | ONGAS 609 P | ONGAS 610 P | ONGAS 611 P | ONGAS 612 P
Efficiency and performance
Heat input (max) | kW | 220 | 293 | 366 | 441 | 512 | 586 | 659 | 730 | 809
Heat input (min) | kW | 24 | 32 | 40 | 45 | 56 | 64 | 72 | 86 | 95
Heat output (max) – Rated (80/60°C) | kW | 214 | 285 | 356 | 428.5 | 498 | 570 | 642 | 709.5 | 788
Heat output (min) – (80/60°C) | kW | 23.3 | 31 | 39 | 43.7 | 55 | 62 | 70 | 84.1 | 93
Heat output (max) – Rated (50/30°C) | kW | 226.5 | 305 | 380 | 453.5 | 530 | 605 | 680 | 762 | 845
Heat output (min) – (50/30°C) | kW | 26 | 35 | 43 | 48.7 | 61 | 69 | 78 | 93.3 | 103
Calorific efficiency – Rated (80/60°C) | % | 97.3 | 97.4 | 97.4 | 97.2 | 97.4 | 97.4 | 97.4 | 97.8 | 97.4
Calorific efficiency – Arithmetic mean (80/60°C) | % | 97.5 | 97.7 | 97.8 | 97.8 | 97.8 | 97.9 | 97.9 | 98 | 98
Calorific efficiency – Reduced (80/60°C) | % | 97.2 | 97.5 | 97.5 | 97.2 | 97.5 | 97.5 | 97.5 | 98.1 | 97.5
Calorific efficiency – Rated (50/30°C) | % | 103 | 103.5 | 103.5 | 102.9 | 103.5 | 103.5 | 103.5 | 104.5 | 104.5
Calorific efficiency – Reduced (50/30°C) | % | 108.7 | 108.5 | 108.5 | 108.3 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5
Calorific efficiency – Partial (37/30°C) | % | 108.8 | 108.6 | 108.6 | 108.5 | 108.6 | 108.6 | 108.6 | 108.7 | 108.6
Gas consumption (max) (G20) | m³/h | 22.5 | 30.2 | 37.8 | 45.9 | 52.9 | 60.5 | 68.1 | 75.4 | 83.6
Gas consumption (min) (G20) | m³/h | 2.5 | 3.3 | 4.1 | 4.7 | 5.8 | 6.6 | 7.5 | 8.9 | 9.9
Gas consumption (max) (G31) | m³/h | 9 | 12.08 | 15.12 | 18.36 | 21.16 | 24.2 | 27.24 | 30.16 | 33.44
Gas consumption (min) (G31) | m³/h | 1 | 1.32 | 1.64 | 1.88 | 2.32 | 2.64 | 3 | 3.56 | 3.96
Pressure loss (ΔT=20 °C) | mbar | 50 | 55 | 60 | 65 | 70 | 76 | 83 | 90 | 100
Nox class |  | 6
Max. central heating temperature | °C | 80
Safety limit temperature | °C | 90
Limit temperature for flue thermostat | °C | 85
Operating pressure (min – max) | bar | 0,8 - 6,0
Water and gas fittings
Water inlet (return) & outlet (flow) |  | DN 80
Gas inlet |  | 1 ¼” |  | 2 "
Flue gas outlet (Ø) | mm | 160 |  | 200
Combustion
Type of appliance |  | B23
Flue gas temperature – Rated (80/60°C) | °C | 73.9 | 75.1 | 75.1 | 76 | 75.1 | 75.1 | 75.1 | 75.3 | 75.1
Flue gas temperature – Reduced (80/60°C) | °C | 55.9 | 58.7 | 58.7 | 58.3 | 58.7 | 58.7 | 58.7 | 59 | 58.7
Flue gas temperature – Rated (50/30°C) | °C | 53.5 | 54.1 | 54.1 | 54.8 | 54.1 | 54.1 | 54.1 | 53.9 | 54.1
Flue gas temperature – Reduced (50/30°C) | °C | 30.2 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.5 | 30.7 | 30.5
Flue gas temperature in DHW mode (average) | °C | 53.4 | 54.6 | 54.6 | 54.9 | 54.6 | 54.6 | 54.6 | 55.5 | 54.6
Flue gas mass flow rate - max | g/s | 93 | 130 | 160 | 183 | 220 | 250 | 312 | 312 | 320
Flue gas mass flow rate - min | g/s | 10 | 12 | 16 | 19 | 25 | 30 | 35 | 42 | 50
CO2 at Pmax | % | 9.3 | 9.3 | 9.3 | 9.4 | 9.3 | 9.3 | 9.3 | 9.1 | 9.3
CO2 at Pmin | % | 9.2 | 9.3 | 9.3 | 9.4 | 9.3 | 9.3 | 9.3 | 9.6 | 9.3
O2 at Pmax | % | 4.2 | 4.1 | 4.2 | 4.3 | 4.1 | 4.1 | 4.1 | 3.8 | 4
O2 at Pmin | % | 4.5 | 4 | 4.1 | 4.3 | 4 | 4.1 | 3.9 | 3.2 | 3.9
CO at Pmax | ppm | 106 | 100 | 98 | 92 | 120 | 110 | 105 | 130 | 120
CO at Pmin | ppm | 18 | 14 | 12 | 6 | 14 | 9 | 6 | 4 | 5
NOx at O2 = 0% (based od GCV) | mg/kWh | 32 | 30 | 27 | 25 | 30 | 26 | 28 | 35 | 32
Electrical
Power supply |  | ~230V / 50Hz | [7 empty] | ~400V / 50Hz
Power consumption | W | 300 | 390 | 460 | 565 | 700 | 850 | 900 | 1030 | 1130
Power consumption simulating boiler hydraulic resistance | W | 430 | 570 | 610 | 815 | 1050 | 1100 | 1200 | 1500 | 1650
Protection level | IP | IPX4D

## 1
ONGAS 600P Serisi |  | ONGAS 604 P | ONGAS 605 P | ONGAS 606 P | ONGAS 607 P | ONGAS 608 P
Efficiency and performance
Heat input (max) | kW | 220 | 293 | 366 | 441 | 512
Heat input (min) | kW | 24 | 32 | 40 | 45 | 56
Heat output (max) – Rated (80/60°C) | kW | 214 | 285 | 356 | 428.5 | 498
Heat output (min) – (80/60°C) | kW | 23.3 | 31 | 39 | 43.7 | 55
Heat output (max) – Rated (50/30°C) | kW | 226.5 | 305 | 380 | 453.5 | 530
Heat output (min) – (50/30°C) | kW | 26 | 35 | 43 | 48.7 | 61
Calorific efficiency – Rated (80/60°C) | % | 97.3 | 97.4 | 97.4 | 97.2 | 97.4
Calorific efficiency – Arithmetic mean (80/60°C) | % | 97.5 | 97.7 | 97.8 | 97.8 | 97.8
Calorific efficiency – Reduced (80/60°C) | % | 97.2 | 97.5 | 97.5 | 97.2 | 97.5
Calorific efficiency – Rated (50/30°C) | % | 103 | 103.5 | 103.5 | 102.9 | 103.5
Calorific efficiency – Reduced (50/30°C) | % | 108.7 | 108.5 | 108.5 | 108.3 | 108.5
Calorific efficiency – Partial (37/30°C) | % | 108.8 | 108.6 | 108.6 | 108.5 | 108.6
Gas consumption (max) (G20) | m³/h | 22.5 | 30.2 | 37.8 | 45.9 | 52.9
Gas consumption (min) (G20) | m³/h | 2.5 | 3.3 | 4.1 | 4.7 | 5.8
Gas consumption (max) (G31) | m³/h | 9 | 12.08 | 15.12 | 18.36 | 21.16
Gas consumption (min) (G31) | m³/h | 1 | 1.32 | 1.64 | 1.88 | 2.32
Pressure loss (ΔT=20 °C) | mbar | 50 | 55 | 60 | 65 | 70
Nox class |  | 6
Max. central heating temperature | °C | 80
Safety limit temperature | °C | 105
Limit temperature for flue thermostat | °C | 75
Operating pressure (min – max) | bar | 0,8 - 6,0
Water and gas fittings
Water inlet (return) & outlet (flow) |  | DN 80
Gas inlet |  | 1 ¼” |  | 2 "
Flue gas outlet (Ø) | mm | 160 |  | 200
Combustion
Type of appliance |  | B23
Flue gas temperature – Rated (80/60°C) | °C | 73.9 | 75.1 | 75.1 | 76 | 75.1
Flue gas temperature – Reduced (80/60°C) | °C | 55.9 | 58.7 | 58.7 | 58.3 | 58.7
Flue gas temperature – Rated (50/30°C) | °C | 53.5 | 54.1 | 54.1 | 54.8 | 54.1
Flue gas temperature – Reduced (50/30°C) | °C | 30.2 | 30.5 | 30.5 | 30.5 | 30.5
Flue gas temperature in DHW mode (average) | °C | 53.4 | 54.6 | 54.6 | 54.9 | 54.6
Flue gas mass flow rate - max | g/s | 93 | 130 | 160 | 183 | 220
Flue gas mass flow rate - min | g/s | 10 | 12 | 16 | 19 | 25
CO2 at Pmax | % | 9.3 | 9.3 | 9.3 | 9.4 | 9.3
CO2 at Pmin | % | 9.2 | 9.3 | 9.3 | 9.4 | 9.3
O2 at Pmax | % | 4.2 | 4.1 | 4.2 | 4.3 | 4.1
O2 at Pmin | % | 4.5 | 4 | 4.1 | 4.3 | 4
CO at Pmax | ppm | 106 | 100 | 98 | 92 | 120
CO at Pmin | ppm | 18 | 14 | 12 | 6 | 14
NOx at O2 = 0% (based od GCV) | mg/kWh | 32 | 30 | 27 | 25 | 30
Electrical
Power supply |  | ~230V / 50Hz
Power consumption | W | 300 | 390 | 460 | 565 | 700
Power consumption simulating boiler hydraulic resistance | W | 430 | 570 | 610 | 815 | 1050
Protection level | IP | IPX4D

## 2
ONGAS 600P Serisi |  | ONGAS 609 P | ONGAS 610 P | ONGAS 611 P | ONGAS 612 P
Efficiency and performance
Heat input (max) | kW | 586 | 659 | 730 | 809
Heat input (min) | kW | 64 | 72 | 86 | 95
Heat output (max) – Rated (80/60°C) | kW | 570 | 642 | 709.5 | 788
Heat output (min) – (80/60°C) | kW | 62 | 70 | 84.1 | 93
Heat output (max) – Rated (50/30°C) | kW | 605 | 680 | 762 | 845
Heat output (min) – (50/30°C) | kW | 69 | 78 | 93.3 | 103
Calorific efficiency – Rated (80/60°C) | % | 97.4 | 97.4 | 97.8 | 97.4
Calorific efficiency – Arithmetic mean (80/60°C) | % | 97.9 | 97.9 | 98 | 98
Calorific efficiency – Reduced (80/60°C) | % | 97.5 | 97.5 | 98.1 | 97.5
Calorific efficiency – Rated (50/30°C) | % | 103.5 | 103.5 | 104.5 | 104.5
Calorific efficiency – Reduced (50/30°C) | % | 108.5 | 108.5 | 108.5 | 108.5
Calorific efficiency – Partial (37/30°C) | % | 108.6 | 108.6 | 108.7 | 108.6
Gas consumption (max) (G20) | m³/h | 60.5 | 68.1 | 75.4 | 83.6
Gas consumption (min) (G20) | m³/h | 6.6 | 7.5 | 8.9 | 9.9
Pressure loss (ΔT=20 °C) | mbar | 76 | 83 | 90 | 100
Nox class |  | 6
Max. central heating temperature | °C | 80
Safety limit temperature | °C | 105
Limit temperature for flue thermostat | °C | 75
Operating pressure (min – max) | bar | 0,8 - 6,0
Water and gas fittings
Water inlet (return) & outlet (flow) |  | DN80
Gas inlet |  | 2"
Flue gas outlet (Ø) | mm | 200
Combustion
Type of appliance |  | B23
Flue gas temperature – Rated (80/60°C) | °C | 75.1 | 75.1 | 75.3 | 75.1
Flue gas temperature – Reduced (80/60°C) | °C | 58.7 | 58.7 | 59 | 58.7
Flue gas temperature – Rated (50/30°C) | °C | 54.1 | 54.1 | 53.9 | 54.1
Flue gas temperature – Reduced (50/30°C) | °C | 30.5 | 30.5 | 30.7 | 30.5
Flue gas temperature in DHW mode (average) | °C | 54.6 | 54.6 | 55.5 | 54.6
Flue gas mass flow rate - max | g/s | 250 | 312 | 312 | 320
Flue gas mass flow rate - min | g/s | 30 | 35 | 42 | 50
CO2 at Pmax | % | 9.3 | 9.3 | 9.1 | 9.3
CO2 at Pmin | % | 9.3 | 9.3 | 9.6 | 9.3
O2 at Pmax | % | 4.1 | 4.1 | 3.8 | 4
O2 at Pmin | % | 4.1 | 3.9 | 3.2 | 3.9
CO at Pmax | ppm | 110 | 105 | 130 | 120
CO at Pmin | ppm | 9 | 6 | 4 | 5
NOx at O2 = 0% (based od GCV) | mg/kWh | 26 | 28 | 35 | 32
Electrical
Power supply |  | ~230V / 50Hz |  |  | ~400V / 50Hz
Power consumption | W | 850 | 900 | 1030 | 1130
Power consumption simulating boiler hydraulic resistance | W | 1100 | 1200 | 1500 | 1650
Protection level | IP | IPX4D